- FACTORY FABRICATED INDUCED DRAFT CLOSED CIRCUIT COOLER

  - General

Furnish and install factory assembled closed circuit cooler of induced draft counterflow design with a horizontal multiple side air entry and a vertical air discharge. The unit shall be completely factory assembled and conform to the specifications and schedules.

The closed circuit cooler shall have the capacity to cool ______ l/sec water / glycol from ____°C to ____°C with a ____°C entering wet bulb temperature.

The total fan power should not exceed ______kW.

The total pump power should not exceed _____ kW.

The total overall unit dimensions should not exceed the following:

Length: _____ mm

Width: _____ mm

Height: _____ mm

The maximum operating weight should not exceed _____ kg.

The unit will be delivered in two parts:

The basin section and the top section.

The unit (top and bottom section) shall be joined together with elastic sealer and bolted together with corrosion resistant fasteners.

Approved manufacturer Evapco – model ESWA ________

  - Thermal Performance – Performance Warranty

The cooler shall be capable of performing the thermal duties as shown in the schedule and on the drawings and its design thermal rating shall be certified by the Cooling Technology Institute (C.T.I.) and the Eurovent Certification Company (ECC). Only models with performance certified by ECC and CTI will be approved.

Manufacturer’s performance guarantee without ECC-CTI certification for the proposed model or an independent field performance test shall not be accepted.

  - Applicable Standards

- Directive 2006/42/EC on Machinery

- Directive 2014/30/EC Electromagnetic Compatibility

- CTI STD 201 Standard for Thermal Performance Certification of Evaporative Heat Rejection Equipment.

- Eurovent Certification operation manual OM-4-2016 CT and Rating Standard RS 9C 001 for Cooling Towers.

- Directive 2014/68/EU Pressure Equipment Directive.

  - Submittals

- The manufacturer shall submit a five year history of the proposed type of closed circuit cooler with a minimum of 10 installations for similar sized equipment.

- Shop drawings: submit shop drawings indicating dimensions, weight loadings and required clearances.

- Product data: submit manufacturer’s technical product data, original selection printouts and clearance requirements.

- Performance data: submit curves showing certified and guaranteed closed circuit cooler performance with variation in outdoor air wet bulb temperature at design air flow and design flow rate. In addition submit performance curves for 90 % and 110 % of design water flow rate, indicating the cooling tower temperatures versus the ambient air wet bulb temperatures.

- Complete noise data sheet for the selected closed circuit cooler.

- Maintenance data for the closed circuit cooler and accessories.

- The closed circuit cooler manufacturer shall provide factory test run certificates of the fans and fan motor.

  - Product Delivery – Storage and Handling

- The contractor shall make the provisions for proper storage at site before installation and handle the product per the instructions of the manufacturer.

- Once installed provide the necessary measures that the units remain clean and protected from any dust and mechanical damage.

  - Quality Assurance

- The manufacturer shall have a quality assurance system in place which is certified by an accredited registrar and complying with the requirements of ISO 9001:2008. This is to guarantee a consistent level of product and service quality.

- Manufacturers without ISO 9001:2008 certification are not acceptable.

  - Warranty

- The products will be warranted for a period of minimum two years from the date of shipment.

- PRODUCT

  - Construction – Corrosion Resistance

- STANDARD EXECUTION – GALVANIZED STEEL Z725

- The structure and all steel elements of the pan and casing shall be constructed of Z-725 hot dip galvanized steel for long life and durability. Alternatives with lower zinc layer thickness and external paint or coating are not accepted as equal.

- The strainer shall be made of stainless steel type 304L or 316L.

- During fabrication all panel edges shall be coated with a 95 % pure zinc compound.

- Casing materials shall be of non-flammable construction.

- OPTIONAL EXECUTION – BASIN IN SST 304L or 316L (except heat exchange coils)

- The structure and all steel elements of the basin coil plenum and louver section shall be made of SST 304L or 316L. Cold water basin will be a welded stainless steel construction.

- Alternatives with hot dip galvanized steel and epoxy coatings in lieu of the SST 304L or 316L are not considered to be equal and are not accepted.

- All other steel components of the casing shall be constructed of Z-725 hot dip galvanized steel for long life and durability. Alternatives with lower zinc layer thickness and external paint or coating or FRP materials are not accepted as equal.

- The strainer shall be made of stainless steel type 304L or 316L.

- During fabrication all galvanized steel panel edges shall be coated with a 95 % pure zinc compound.

- Casing materials shall be of non-flammable construction.

- OPTIONAL EXECUTION – COMPLETE UNIT IN STAINLESS STEEL SST 304L or 316L (except heat exchange coil(s))

- The structure and all steel elements shall be made of SST 304L or 316L.

Cold water basin will be a welded stainless steel construction.

- Alternatives with hot dip galvanized steel and epoxy coatings in lieu of the SST 304L or 316L are not considered to be equal and are not accepted.

- The strainer shall be made of stainless steel type 304L or 316L.

- Casing materials shall be of non-flammable construction.

  - Construction – Seismic and wind load resistance

- The structural design must be designed in accordance with IBC2015 with and Importance factor (Ip) of _____, a seismic factor (SDS) up to ____ g a wind load up to ____ kN/m²

  - Basin Section

    - Closed Circuit Cooler Basin

- Standard basin accessories include: overflow, drain, strainer and brass make up valve with plastic float ball.

- The entire pan area shall incorporate a sloped basin design to prevent sediment built up, biological film and standing water.

- The entire pan area shall be enclosed and protected from exposure to environmental elements by solid panels.

- The minimum distance between the heat exchange coil and the basin floor shall be 200 mm to allow easy cleaning.

- The basin bottoms shall be sloped and stepped to provide drainage of the complete basin section.

- The basin can be inspected, cleaned and completely flushed without the need to enter the unit.

    - Air Inlet Louvers

- The air inlet louvers shall be constructed of UV inhibited polyvinyl chloride (PVC) and incorporate an interlocking design.

- The louvers shall have a minimum of two changes in air direction to prevent splash out and block direct sunlight to the circulating water and heat transfer system.

- The louvers will have a 19 mm opening to prevent debris to enter the basin.

    - Water Circulation Pump

- The pump(s) shall be a close coupled, centrifugal type with mechanical seal, installed

vertically at the factory to allow free drainage on shut down.

- A ____ kW totally enclosed motor(s) suitable for outdoor service shall be furnished.

- The motor shall be suitable for the following power supply :

____volts, ____hertz and ____ phase.

  - Coil Section

    - Heat Transfer Coil

- The closed circuit cooler shall use internally enhanced heat exchange coils of a tightly spaced elliptical tube design.

- The heat exchange coils shall be made of all prime surface, encased in a steel framework and hot dip galvanized after fabrication as a complete assembly.

- The heat exchange coils shall be air pressure tested under water.

- The design and manufacturing process shall be approved and in accordance with the “Pressure Equipment Directive” – PED2014/68/EU.

- The manufacturer shall be responsible for the manufacturing and performance testing of the entire heat exchange coil, this to assure single source responsibility.

- The coil assembly shall be totally enclosed and completely protected from sunlight exposure, environmental elements and debris.

- The sheltered enclosure shall eliminate natural drafts across the coil. Closed circuit coolers where the heat exchange coils can be subject to natural draft shall be equipped with discharge dampers.

- The heat exchanger shall use complete sensible cooling for minimum potential for scale build up.

- The pressure drop of the process fluid through the coil shall not exceed ___kPa.

OPTIONAL - Heat Transfer Coil in SST 304L or 316L

- The closed circuit cooler shall use heat exchange coils of a tightly spaced elliptical tube design.

- The heat exchange coils shall be made of SST 304L or 316L encased in an SST 304L or 316L framework and externally passivated after fabrication as a complete assembly.

- The heat exchange coils shall be air pressure tested under water.

- The design and manufacturing process shall be approved and in accordance with the “Pressure Equipment Directive“ – PED2014/68/EU.

- The manufacturer shall be responsible for the manufacturing and performance testing of the entire heat exchange coil, this to assure single source responsibility.

- The coil assembly shall be totally enclosed and completely protected from sunlight exposure, environmental elements and debris.

- The sheltered enclosure shall eliminate natural drafts across the coil. Closed circuit coolers where the heat exchange coils can be subject to natural draft shall be equipped with discharge dampers.

- The heat exchanger shall use complete sensible cooling for minimum potential for scale build up.

- The pressure drop of the process fluid through the coil shall not exceed ……kPa.

  - Closed Circuit Cooler Top Section

    - Heat Exchange Fill

- The closed circuit cooler fill shall be PVC (Polyvinyl Chloride) of cross fluted design for optimum heat transfer and efficiency.

- The cross fluted sheets shall be bonded together for maximum strength and durability. Fill packs which are not bonded are not allowed. The fill sheets will be bonded together in such a way that the structural integrity of the fill makes the fill useable as an internal working platform.

- The PVC fill shall be self extinguishing for fire resistance with a flame spread rating of 5 per ASTM  E 84 – 81a.

- The fill shall be resistant to rot, decay or biological attack.

- The closed circuit cooler manufacturer shall be responsible for the manufacturing and performance testing of the fill. This is to assure single source responsibility.

- The casing shall totally encase the complete fill section to protect the complete fill from direct atmosphere contact.

- The construction of the unit shall allow easy removal of the fill bundles for maintenance purposes.

- The fill shall be elevated a minimum of 600 mm above the coil to facilitate inspection.

    - Water Distribution

- The water distribution system shall be completely enclosed and protected from sunlight        exposure, environmental elements and debris. Water distribution systems with direct        exposure to the environment are not allowed.

- The spray header and branches shall be constructed of Schedule 40, Polyvinyl Chloride (PVC) pipe for corrosion resistance.

- The water shall be distributed by precision molded ABS spray nozzles with large orifice openings and integral sludge ring to eliminate clogging.

- The nozzles shall be threaded into the water distribution piping to assure positive positioning and easy removal for maintenance. Snap in or strapped on type nozzles are not accepted.

    - Drift Eliminators

- The drift eliminators shall be constructed entirely inert polyvinyl chloride (PVC) that has been specially treated to resist ultra violet light.

- Assembled in easily handled sections, the eliminator blades shall be placed on 25 mm centers and shall incorporate three changes in air direction to assure efficient removal of entrained moisture from the discharge air stream.

- The maximum drift rate shall not exceed 0,001 % of the circulating water rate.

- The Drift Eliminators shall be certified according to Eurovent Standard OM-14-2014.

    - Access Door

- A large hinged access door shall provide access to the fan section for maintenance.

  - Mechanical Equipment

    - Axial Propeller Fan(s) (standard)

- Fan shall be heavy duty wide chord axial propeller type, statically balanced and constructed of extruded aluminum alloy blades.

- Fans shall be installed in a closely fitted cowl with venturi air inlet for maximum fan efficiency.

- Each fan blade shall be individually adjustable.

- The fan cowl shall be covered with a heavy gauge hot dip galvanized steel wire fan guard.

- The fan – drive system (fan – drive – motor) shall be factory mounted, adjusted and undergo a trial run in the factory before shipment.

    - Axial Propeller Fan(s) - Low Sound Fan (optional)

- Fan shall be heavy duty wide chord axial propeller type, statically balanced and constructed of extruded aluminum alloy blades.

- Fans shall be installed in a closely fitted cowl with venturi air inlet for maximum fan efficiency.

- Each fan blade shall be individually adjustable.

- The fan cowl shall be covered with a heavy gauge hot dip galvanized wire fan guard.

- The fan – drive system (fan – drive – motor) shall be factory mounted, adjusted and undergo a trial run in the factory before shipment.

    - Axial Propeller Fan(s)  - Super Low Sound Fan (optional)

- Fan shall be extremely wide chord axial, heavy duty propeller type, statically balanced and made of FRP.

- Fans will be installed in a closely fitted cowl with venturi air inlet for maximum fan efficiency.

- The fan cowl shall be covered with a heavy gauge hot dip galvanized wire fan guard.

- The fan – drive system (fan – drive – motor) shall be factory mounted, adjusted and undergo a trial run in the factory before shipment.

    - Bearings and Drive

- The fan shaft(s) shall be supported by heavy duty, self-aligning ball type bearings with cast iron housings and lubrication fittings for maintenance.

- The grease fittings shall be extended to the outside of the unit.

- The bearings shall be rated for an L-10 life of 75,000 hours.

- The fan drive sheaves shall be aluminum alloy.

- The belt shall be a multigroove belt system, constructed of neoprene with polyester cords and designed for 150 % of the motor nameplate horsepower.

    - Motor (Models  ESWA 72 , 96 and 142)

- The fan motor shall be Totally Enclosed Fan Cooled (TEFC), squirrel cage, ball bearing type motor.

- The motor shall be specially designed for cooling tower use with moisture protection on the windings, shaft and bearings.

- The motor shall be minimum IP 55 degree of protection, Class F insulation, Service Factor 1 and selected for the appropriate cooling tower duty and the correct ambient temperature but minimum 40°C.

- Motor bearings shall be greased for life or external grease nipples shall be provided.

- The motor shall be mounted on an adjustable heavy duty steel motor base.

- A protective cover shall shield the motor and sheave from the weather.

- The motor power supply shall be …… volts, ….. hertz and ….. phase.

    - Motor (Models ESWA 144 and 216)

- The fan motor shall be Totally Enclosed Air Over (TEAO), squirrel cage, ball bearing type motor.

- The motor shall be specially designed for cooling tower use with moisture protection on the winding, shaft and bearings.

- The motor shall be minimum IP 55 degree of protection, Class F insulation, Service Factor 1 and selected for the appropriate cooling tower duty and the correct ambient temperature but minimum 40°C.

- Motors bearings shall be greased for life or external grease nipples shall be provided.

- The motor shall be mounted on an adjustable heavy duty steel motor base.

- The motor base shall be able to swing to the outside of the unit for repair or removal.

- The motor power supply shall be …… volts, ….. hertz and ….. phase.

  - Sound Levels

The maximum sound pressure levels (dB) measured 15m from the closed circuit cooler operating at full fan speed shall not exceed the sound levels detailed below.

| Location | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | dB(A) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Hz | Hz | Hz | Hz | Hz | Hz | Hz | Hz |  |
| Fan Discharge |  |  |  |  |  |  |  |  |  |
| Air inlet/end |  |  |  |  |  |  |  |  |  |

Measurement in accordance with ISO 3744.

- ACCESSORIES (optional)

  - Electric Heaters

- The closed circuit cooler cold water basin shall be provided with an electric heater package to prevent freezing of the water in the cold water basin.

- The electric heater package includes: electric heater elements and a combination of thermostat and low water level cutoff.

- The heaters shall be selected to maintain 4°C basin water temperature at …..°C ambient.

- The heater(s) shall be ……V / …… phase / ….. Hz electric power supply.

  - Five Probe Electric Water Level Control Package

- The closed circuit cooler manufacturer shall provide an electric water level control package instead of the mechanical float valve arrangement.

- The package consist of the following elements :

- Multiple heavy duty stainless steel 316 static probes mounted in a stilling chamber outside the unit. Electrodes or sensors mounted inside the unit are not accepted as their operation will be disturbed by the moving water in the basin.

- An ABS, IP 56 case contains all the contactors for the different level probes and will provide an output signal of a relay for automatic filling and two relays for alarm levels.

- The power supply to the control package is 24 Vac / 230 Vac - ….. Hz .

- A weather protected solenoid valve (PN16) for the water make up ready for piping to a water supply with pressure between 140 kPa and 340 kPa.

  - Vibration switch

- A vibration limit switch shall be installed on the mechanical equipment support and wired into the control panel. The purpose of this switch is to interrupt power to the motor in the event of excessive vibration.

- The switch shall be adjustable for sensitivity, and shall require manual reset.

  - Vertical Access Ladders

    - A vertical type ladder arrangement which provides easy access to the water distribution system and drive components shall be provided with the cooling tower.

    - The ladder will be completed with a safety cage for safety purposes.

    - Ladder and safety cage shall meet CE requirements.

    - Ladders shall be made of aluminum.

  - External Service Platform

- The closed circuit cooler shall be supplied with an external service platform.

- The external service platform will be self-supporting and includes access ladders with safety cage to the platform and handrailing.

- The external service platform will be installed in front of the fan access doors.

- The platform shall meet CE requirements.  Platforms shall be made of hot dip galvanized steel.

  - Multipurpose Davit

- The closed circuit cooler will be completed with a davit to facilitate the removal of fan(s) and fan motor(s).

- The davit and bracket are constructed of aluminum and are mounted on the side of the unit.

- The fan motor davit ships loose with the unit and is installed in the field.